## UMS Queries Log
UMS Queries Log
At the June 2021 UMSUG Meeting (UMSUG132), the UMSUG agreed that Elexon should maintain a log of queries raised by Elexon or UMSUG members around controversial Charge Code applications or related UMS issues. The aim of the UMS queries log is to understand the details of any contentious applications or topics, the UMSUG’s responses and the outcome from Elexon. This can then be used as a knowledge base for both Elexon and the UMSUG for future queries of a similar nature.
Date | Issue | UMSUG comments | Outcome | Further UMSUG comments
UMSUG September - 133 | CMS nodes are being powered constantly by new types of LED drivers that have recently become available. This energy is not currently being fully accounted for. | UMS member to bring paper to UMSUG133 (UMSUG133/04) | UMS member to complete the OID red-lining to clarify the testing requirements to ensure that the energy consumed by permanently powered LED Drivers is allocated correctly.
UMSUG September - 133 | A manufacturer asked for clarification on what the upper and lower variance limit would be for a 230V supply. | • The UMSUG referred us to “The Electricity Safety, Quality and Continuity Regulations 2002” at para 27.(3) (b) which states that ‘in the UK, the declared voltage and tolerance for an electricity supply is 230 volts -6%, +10%’. This gives an allowed voltage range of 216.2 volts to 253.0 volts. • The UMSUG noted that the circuit watts for a piece of equipment are taken at 240V, because it was decided that 240V was a reasonable average of the volts at which LV networks operate. They explained that it is very likely that equipment connected to the network a short distance from the substation will receive a supply at a higher voltage than something connected at the end of a long spur of the network because of the voltage drop. | We relayed the UMSUG response to the applicant. Applicant responded saying the equipment being installed in the cabinet do have their own charge codes and they will be submitting an inventory to UKPN for all three charges codes (fans + equipment). The UMSUG were satisfied with this.
UMSUG September - 133 | A manufacturer queried whether they can have a reduced testing scope in terms of number of samples required for their CCTV equipment. This is due to there being various configurations of the same equipment, but each with negligible variances in load between them (e.g. Power over Ethernet (PoE), and Infra-red and Infra-red white light versions). | • There were no objections to a proposed reduced testing scope of: 3x samples for the base model, 3x samples for both the IR and IRWL versions, and 2x samples to confirm the difference between the PoE version and the 24v DC version. This is a reduction from the original 30 required testing samples. • The UMSUG had a follow up query for the manufacturer, asking how exactly the PoE version works, and how the energy would be accounted for. | • We provided the manufacturer with the UMSUG’s views and the manufacturer noted they will base their testing on the proposed reduced testing scope. • The manufacturer responded to the UMSUG’s query on PoEs, stating that the consumption of the PoE would be accounted for in additional equipment that provides that power (typically a PoE injector ‘brick’). Although different 3rd party injectors will vary slightly in circuit design, the mains draw on the whole should be consistent, as the camera’s fundamental operation and power will not change. The manufacturer noted they will conduct testing with their own PoE injector device that they offer to customers as an option.
UMSUG September - 133 | The applicant have developed a system to grow plants on lamp posts called Living Pillars. They are designed primarily to run off the solar panel but have a battery to power the irrigation pump and the GSM microprocessor. In streets with high buildings they have found that there is not always enough sunlight (especially on cloudy days), so they need to top up the charge from a mains powered source from the feed to the lights. - They have questioned how will they replicate their power requirements for UMS testing, given that the draw would not be constant and depend on the solar radiation on the day. | The UMSUG agreed that this equipment does not seem suitable for UMS.C8 • The UMSUG questioned why a watering system needs a GSM module, noting that the brochure describes it as retrofit to existing columns so they do not see the solar panel powering the light. They suggested that the pump would be needed more in the summer when the solar panel will be operating well, rather than a cold/cloudy day which in this country often is also damp – needing less pumping. There is also the safety concern of mixing mains power with water on metallic street furniture. They also suggested that they could increase the size of solar panel and battery in the darker locations. • The UMSUG noted that the objectives might be better achieved by hanging the equipment off buildings with a ready source of metered energy. | We provided the manufacturer with the views of the UMSUG. The manufacturer advised that they plan to go ahead with their Charge Code application.
UMSUG September - 133 | Elexon received an application for an automatic ventilation/filtering system. They had been given a local miscellaneous charge code on the condition that they apply for a national charge code. - Basic consumption: 45W - Irrigation and ventilation (depending on weather conditions): 356W (theoretical max value at max rpm of ventilation (standard ventilation is set at 500 rpm from max 1450 rpm) - LED control (day/night, controllable by client): 115W - Total max Wattage: 525W - Power supply box can take 840Watts (600W+240W LED) - The variables in the operation is the surrounding weather of the CityTree. If it is dry around the CityTree, the moss is watered more frequently, which leads to a higher power consumption of the irrigation system. The ventilation is set to a certain schedule, for best effect and filter performance. The UK climate has little to no effect on how the CityTrees work as it are measuring a “micro climate” around the CityTree and control it accordingly. The difference between the CityTree standing in a windless yard or on a street with a lot of sun exposure and wind, makes more difference than the CityTree being set up in different climate regions e.g. in London or in Newcastle. | • The UMSUG agreed that the applicant should go down the metered route, based on the information provided. They noted that the consumption could vary depending on which side of the street the equipment is situated and the variable element of the load is the greater part of the total load. They directed us to the BEIS guidance which states that ‘in determining if a load meets this criterion BEIS encourage a pragmatic approach to equipment which will, for the majority of time, require a constant load but may have small variations in load from time to time that are insignificant in terms of overall kWh consumption taken on an annual basis’. • The UMSUG noted that they could only arrive at a considered view once there is test data to review. With the 120W being stated as average, the concern is the range of values, especially in each settlement period, as this would obviously have a knock-on effect with DUoS charges if it was considerably higher in some periods and lower in others | • Elexon informed the applicant that they will have to go down the metered route for their equipment. • The UMSO who had issued a local miscellaneous charge code agreed they needed to make alternative metered arrangements.
UMSUG December - 134 | Elexon received a request from a company who is receiving a number of ‘one-off’ signs (VMS) which require a charge code. They have advised that it is very unlikely that any more of these signs will ever be made so they only have single units for the UMSUG testing. They have already tried going down the local code route but it wasn’t suitable. They noted that although these signs are only ‘one offs’ they are still built to a very high ‘motorway grade’ so the UMSUG route is definitely the route they need to go down. |  | We advised that as it is a ‘one-off’ sign only for installation in one area, that the UMSO should be able to agree a local charge code which should not require test data, however it is down to the individual UMSO on how they conduct their own local charge code processes.
UMSUG December - 134 | Elexon received an application to issue charge codes for smart city sensor devices, which interface into a controller, for detection of vehicles or environmental air quality parameters. | The UMSUG felt a discussion on the best approach was needed before allocating Charge Codes. The following points were raised; •The interpretation of this equipment is that the A670 base unit is plugged into a NEMA socket in place of the existing PECU. Various sensors can the be added to the base unit depending on what the customer wants. At this moment they are just looking for Air Quality and Traffic Monitoring. • If the base unit is going to replace the PECU, they can't see a photocell anywhere and the sensor plugs in where the photocell would normally be i.e. on top. If there is a photocell, is the base unit configurable to various lux levels to match the customer’s existing switch regimes? • They don't think giving this equipment a single charge code is the right way to go. They think the base unit should get a control charge code as it replaces the PECU. The different plug-in sensors can then then be allocated miscellaneous charge codes to match their function. The miscellaneous codes might need reviewing to cover these functions or a catch-all Smart City Sensors code added. • They suggest more testing is required to determine the circuit watts of the base unit, which can then be used to extrapolate the charge code for the base unit and the two sensors. If the complete unit is given a Charge Code then there will be no control charge code for the streetlight inventory entry and a second line in the inventory for the complete unit (base and sensor). | • Elexon relayed the UMSUG comments and the applicant resubmitted the application and attached the additional power measurement data for the base controller without sensor. • The applicant also clarified that the base unit contains an on-board photocell and it would be configurable to match various lux levels to match existing pre-approved switch regimes. While some clients will indeed employ this controller in the NEMA socket atop the lighting assets, some have decided to install a stand-alone NEMA, separate from the lantern, to deploy the controller and sensor. In that instance, there would be no switch regime to reference.
UMSUG December - 134 | Elexon received a query asking us to confirm that once an unmetered supply has erroneously turned into a metered supply it is “impossible” to return. On that basis it appears, the only way to progress this is to disconnect the existing MPAN and to create a new MPAN. This needs to be done in conjunction with UKPN. | The UMSUG clarified the issue is with the Metered Id which is initially set to Metered and can then be updated to unmetered but this can only happen once. The UMSUG confirmed that it needs to be disconnected and a new UMS MPAN needs to be created. | Elexon relayed the UMSUG response to the applicant.
UMSUG December - 134 | Elexon received an Standard Charge Code application for a Ventilation Unit and submitted it to the UMSUG to review. | UMSUG commented that the applicant should provide a little more context. • What’s going to be in the cabinet that requires cooling. • Does whatever’s going to be in the cabinet have a charge code? | Elexon relayed the UMSUG response to the applicant. Applicant responded saying the equipment being installed in the cabinet do have their own charge codes and they will be submitting an inventory to UKPN for all three charges codes (fans + equipment). The UMSUG were satisfied with this.
UMSUG December - 134 | A manufacturer asked for testing guidance for their LEDpod system, which would vary depending on the number of LEDpods connected to the single mains power supply. | The UMSUG suggested that testing is carried out with a range of LEDpods connected at say 10 LEDpods connected intervals. • The test results will then give a power curve. If on the power curve you have test results at 30 and 40 LEDpods powered, if a customer has an installation with 35 LEDpods connected, the manufacturer can give the customer a generic LED charge code that equates to where 35 LEDpods sit on the curve. • If they want to go for dimming as well then there ought to be evidence that when dimming is employed the power take drops as expected. | Elexon relayed the UMSUG response to the applicant.
UMSUG December - 134 | A manufacturer asked whether Elexon would accept data from their in-house test lab which is a CTF3 level manufacturer laboratory of TUV Hungary. Its internal audit is always performed according to ISO 17025 but the lab has no official accreditation for ISO 17025. | The UMSUG advised that the test house should be accredited, however we raised the issue that we have previously accepted test data from test houses that are not accredited, as the Operational Information Document states ‘…or other test houses agreed by BSCCo'. | Awaiting UMSUG response but in the meantime we have let the applicant know that the test house should be accredited to ISO 17025.
UMSUG March - 135 | Elexon received a test data query from an accredited test house, relating to the test data supplied in the reports they send to clients. They include two sets of results; total Watts and VA and fundamental Watts and VA. Total Watts and VA (include Fundamental + Harmonic + Noise measured from the equipment under test) and Fundamental Watts and VA (All distortion generated from the equipment under test is removed). This is a unique feature that their power analyser possesses and their question relates to which Watts and VA results are needed for the Charge Code calculation. The operational document simply states that the VA and Watts figures shall be recorded and they are assuming when the document was created it was based on an ideal load being resistive, therefore the mathematical product of voltage and current? They have asked if this was the case would it be correct to report with the distortion removed i.e. fundamental measurements based on the power of the signal at the fundamental frequency of 50Hz. They would like to check as power factor is obviously affected depending on the route taken. | UMSUG advised that unmetered arrangements are seeking to replicate what an energy meter in a premises would measure (in the absence of a meter). Metering legislation sets out what should be measured. So what they report should be equivalent to what an energy meter would record. | Elexon relayed the UMSUG response to the applicant.
UMSUG March - 135 | Elexon received a query from a testing lab regarding Tubular LED Lighting. The lighting comes in 7 colours and is rated by the supplier at 4 Watts per meter. The LED lighting has a power supply driver and there are 30 LEDs per meter. The LEDs are non-replicable. The installation which requires a charge code is a 50 metre bespoke design in one colour. Initial questions: 1. Do they test 1 sample of each colour or just 1 sample to cover the colour range as they all have the same rating from the supplier. 2. What length do they test 1 metre/ 50 metres or 10 metres and arrive at a rating per metre by dividing by 10? Responses: - Their laboratory has been in discussion with the manufacturer of the Rope lighting who advised that there is no difference in each colour model. They feel that testing 5 samples at 10 metre length of the colour to be used in the final installation will give a representative sample suitable for arriving at a measurement per metre. The final installation can have a charge code calculated from our test results. | • If they test 1 metre connected to the power supply driver and use that to give a circuit watt rating per metre, the power losses from the driver are going to be greater per metre, than if they test with 10 or 50 metres connected. If they test 5 samples at 10 metres each with its own driver, multiplying that by five will not give an accurate circuit wattage for 50 metres which will have only one driver. i.e. 5 lots of transformer losses instead of one. • As seen with traffic lights, the power requirement for an LED varies with colour, and they suspect that this is going to be programmable so that the colour varies whilst connected cycling through a range of colours. If a Charge Code is going to be issued based on a single colour, that colour should be included in the description. • Rather than UMSUG trying to second guess how the lighting works, they suggested that the applicant puts forward a rationale that explains these variables; i.e. - What does the factory testing show the circuit watt rating is for 1 metre connected, 10 metres connected and so on. - What is the difference in power between the colour with the lowest power requirement and the colour with the highest power requirement. Once we have details from the manufacturer that gives UMSUG an idea how it performs then we can advise the test house to conduct tests accordingly. • If it’s going to be illuminating buildings or shopping centres, take a supply from the building’s meter. If it’s going to be Festive Lighting then use the rationale in the OID. • If this is a single installation with a requirement for a 50 metre length in a single colour it really lends itself to agreement with the UMSO on a miscellaneous code or a meter. | Elexon relayed the UMSUG response to the applicant and advised that as the power consumption varies with colour, it really lends itself to an agreement with the UMSO. If something is only being installed in one UMSO area, they might be able to get a Local Miscellaneous Charge Code without having them published in the BSCCo Charge Code Spreadsheet. In other words, a national Elexon Charge Code application would not be required.
UMSUG March - 135 | Elexon received a query regarding the test procedure for traffic radar detectors. The radars operate on a DC voltage between 12-30v which is generally taken from a traffic signal controller. They wanted to know what process they need to follow to obtain Elexon Charge Codes for this equipment given that it is DC and takes power from a ‘host’ traffic signal controller. | UMSUG advised that this scenario is the same as traffic signal aspects or any other traffic signal equipment taking a DC supply from the traffic signal controller. This is covered by the third bullet point of para. 3.2 of the OID. So test at DC and provide DC test results, then Elexon adds a nominal 10% to cover transformer power losses. | Elexon relayed the UMSUG response to the applicant.
UMSUG March - 135 | Elexon received a query regarding the test procedure for Belisha Beacons. The OID includes the following; Belisha Beacons shall be tested at a constant load with the lamp constantly on (i.e. no flashing). BSCCo will then take 62% of the full Circuit Watts to account for the lamp flashing. Alternatively, the energy consumed over the period of say 10 minutes will give the average consumption while flashing. When submitting test evidence, the method of test should be clearly stated. The applicant asked for advise on the format when submitting the energy consumed over 10 minutes. | UMSUG advised that the test house needs to measure the time accurately (in part of hours) and measure the Watt-hour accurately. Average wattage over 10min = Watt-hour / time (in hours). Different voltages and different samples will each need measuring and reporting. | Elexon relayed the UMSUG response to the applicant. Unfortunately they do not have a calibrated energy meter to obtain an accurate W/hr reading so they confirmed they will have to go with the 62% method.
UMSUG March - 135 | Elexon received a query from a manufacturer of universal EV charging and docking solutions for electric bikes and scooters. The manufacturer is looking to obtain the required certification for UMS. | A Meter Administrator advised that clarification would be required to see if their product would qualify for mCMS. The charging points would qualify for an Unmetered Supply but we need to confirm if the mCMS test specification (set up for EV charging) can accommodate charging points for bikes and scooter. For EV charging, there is one socket for one car. However, bike charging points can have one socket charging multiple bikes. | Elexon asked the prospective applicant for clarification.
UMSUG March - 135 | At the December UMSUG meeting, Elexon received a query regarding CCTV cameras with infrared lamps. An UMSUG member wanted to know how infrared lamps were accounted for in the calculation. | Elexon responded that several Charge Codes have been approved for cameras with infrared lamps and 50% of the lamp test data was used in the calculation to account for the night mode. The UMSUG agreed that a 50% weighting was reasonable. | As agreed at the UMSUG meeting, Elexon added to the Queries Log and will include clarification in the next OID update.
UMSUG June- 136 | Elexon reveived an Generic LED Charge Code which exceeded 1000 watts, Elexon recommend the upper limit is increased further to 1500 watts. | UMSUG agreed for the upper limit to be increased | The two Charge Code ranges that exceeded the new 1000W upper limit had been withdrawn from the cycle and were processed in the next application cycle as the Upper limit was increased
UMSUG June- 136 | Elexon received an Standard charge code application for a main power supply but were unsure how to proceed and asked UMSUG for assistance | UMSUG advised you cannot give a power supply unit a Charge Code, as the power supply can be used to power any equipment and thus the power load will vary depending on the load of the equipment connected. The Charge Code must relate to the connected item as a complete unit - the CCTV. If the manufacturer requires a mains connected CCTV, rather than solar, then the Charge Code must relate to the CCTV and not the power supply. | Elexon relayed this to the applicant who confirmed it will be the CCTV they are wanting a charge code for and proceeded with the application
UMSUG June- 136 | Elexon received a standard charge code application for a Network camera whereby there was test data for the night time operation (IR on) but for the day time operation only the LoRa Gateaway was measured | UMSUG advised the proposed Charge Code provided is incorrect. The night time operation (IR on) test is correct as the Light Sensor is covered and IR operational, the day time operation is incorrect as only the LoRa Gateway has been measured in the test. The day time operation should be the same test as the night time but with the Light Sensor uncovered (IR off). | Elexon relayed this to the applicant and removed the application from the cycle, the applicant has resubmitted the correct data in a later cycle
UMSUG September - 137 | Elexon received a query regarding testing requirements for a unit that was being fitted to carry out automated safety testing, the units would carry out intermittent testing and then report these via a GPRS modem – in the case of one unit it measures a series of parameters every 10 minutes and in the case of the other it carries out a loop impedance test every 24 hours, they wanted to know the best way to test the units | UMSUG advised testing for 24hrs (maybe doing this 2 or 3 times to see if the reading change) is a good idea. Then determine an average 30 minute value for the code At least the units will cycle as it is not on constantly. It could then be given a code that would work on the regime 001. | Elexon relayed this to the applicant who informed us the testing lab have issues running tests for 24 hours, and proposed an alternative approach- one 30 minute test when it is not running the test and one 30 minute test during which it will run a test. We can then take the “no-test” result and multiply that by 23 and then add the “test” result. If we then divide by 24 we will get the average 30-minute usage, we forwarded this to UMSUG who agreed with the approach
UMSUG September - 137 | Elexon reveived a query asking if there were any plans to introduce coding which allows for classifications below 1W for LED Range units | UMSUG advised there were many factors to consider and it would be best to discuss during the UMSUG Meeting- Elexon to bring a paper to allow decimal ratings in the Generic LED range | Elexon to bring a paper to UMSUG
UMSUG September - 137 | Elexon received a query regarding advise on the best way to treat extra low voltage LED Module strings running from step down transformers | Elexon Design Authority SME advised if these handrails are bespoke, then the UMSO should provide a UMSO Specific Miscellaneous Charge Code for each configuration. If they have a standard length then this can be tested and provided with a national Charge Code. UMSUG advised a discussion is needed during the UMSUG meeting | To be discussed at UMSUG
UMSUG September - 137 | Elexon received a query whereby the applicant requested if he could submit test data for only 3 samples | UMSUG advised, although this been allowed in the past but this was due to a unique piece of equipment which was extremely large and was for a very low production run, if not a single unit. In this case they would expect the OID to be followed and five units submitted for testing, unless there is a very strong case from the manufacturer. Going through a development phase is, in their opinion, not a strong case. | Elexon relayed this to the applicant