## Slide 1
Technical Assurance Agent
Annual Report 2016-2017
July 2017

## Slide 2
The Scope of This Year’s Audit
July 2017

## Slide 3: Scope of Audit
Inspection visits undertaken in this audit year
  1,518 SVA HHMS
    1,413 – Main sample
    102 – Specific sample
    3 – Targeted inspection
  61 CVA HHMS
    60 – Main sample
    1 – Targeted inspections

## Slide 4: No Access Performance
Chart: SVA and CVA No Access Performance
| 2014/2015 | 2015/2016 | 2016/2017
SVA | 0.07 | 0.09 | 0.1
CVA | 0.01 | 0.01 | 0.26

## Slide 5: LDSO Attendance
Many Suppliers are still not complying with the requirements of BSCP27. Mandatory requirement for Suppliers to arrange LDSO attendance where the Metering Equipment is HV
Supplier pre-inspection field flagged as “Not Applicable”
We now record those inspections where Measurement Transformers were not accessed
344HHMS inspected, CT/VT rating plate not accessed

## Slide 6
The Health of the Market
July 2017

## Slide 7: The Health of the Market
SVA
Category 1 non-compliance reporting shows an increase from 20 last year to 31 this year.
We have noted the following trends:
  Reduction in timing errors
  Reduction in incorrect CT ratio selection
  Increase in Metering Equipment recorded errors

## Slide 8: The Health of the Market
Chart: SVA Category 1 Non-Compliances
| 2014/2015 | 2015/2016 | 2016/2017
1.01 | 2 | 2 | 5
1.02 | 8 | 5 | 14
1.03 | 12 | 8 | 4
1.04 | 3 | 5 | 4
1.06 | 1 | 0 | 4

## Slide 9: The Health of the Market
SVA
Specific Sample
We identified 3 Category 1 non-compliances linked to:
  Incorrect VT ratio selection
  HHDC D0268 error
  Outstation time drift

## Slide 10: The Health of the Market
SVA
Issues detected and what do they mean?
  Removed and blown fuses
  CTs being open circuit or shorted out
  Wiring faults
  Faulty meters
  CT orientation

## Slide 11: The Health of the Market
SVA
Continued improvement in the rectification of Category 1 non-compliances has not been maintained, rising from 12 working days last year to 16 working days this year
There remains a number of unresolved Category 1 non-compliances recorded this year at the time of writing our report
Two unresolved Category 1 non-compliances remaining from previous audit years

## Slide 12: The Health of the Market
CVA
Two Category 1 non-compliances have been recorded this year
The ELEXON Trading Disputes team deem there is no impact to Settlement
11 Category 1 non-compliances recorded since 2007
Data checks (CDCC) identified two non-compliances.
Category 2 count has fallen for the 2nd consecutive year

## Slide 13
Key Audit Issues
July 2017

## Slide 14: Key Audit Issues
Commissioning
SVA
  This year’s results are once again a concern
  How are parties performing against P283?
  Specific Sample 2017-2018
CVA
  Improved figures
  Pre-1993 Registration

## Slide 15: Key Audit Issues
COMMISSIONING
Over 70% of HHMS audited had missing, incorrect or incomplete commissioning (SVA)
  HHMS inspected that were commissioned after the introduction of P283 show a 60% commissioning failure rate
Figures continue to suggest a weakness by Market Participants with their commissioning processes

## Slide 16: Key Audit Issues
Chart: SVA Category 1.04 non-compliances
| 2014/2015 | 2015/2016 | 2016/2017
Raised | 3 | 5 | 4

## Slide 17: Key Audit Issues
ME Failures
A significant increase in ME failures recorded this year.
Undiscovered?
HHDC Documentation errors
Increased numbers
Root cause

## Slide 18: Key Audit Issues
Measurement Transformer Certificates
665 Category 2.16 non-compliances identified. The figure remains consistently high year on year. (663 remain unresolved)
Overall Accuracy confirmation without Certificates
ME rating plate accessibility
Meter compensation

## Slide 19
Any Questions?
July 2017

## Slide 20
Technical Assurance Agent
Annual Report 2016-2017
July 2017